## Ship_System particulars
Ship/System Particulars
Ship Name: |  | Date(s):
IMO No.:
Details of Automatic Sprinkler System(s) Installed: | [7 empty] | Initial
Basic
Make | Type | Serial number(s) | Date Installed | Pilot Pressure | Maximum Operating Pressure | Total number of Nozzles/Sprinkler heads installed | Total number of sections | Extended
SILVANI ANTINCENDI S.p.A, ITALY | SILVANI F1, Pendent | Not available | 1996 | Operation Pr: 7 Bar | Max. Oper. Pr.: 9 Bar | Approximately 500 nos12 sections | 12 sections | Initial and Basic
| Heat breakable bulb |  |  |  | Design Pressure: 16 bar | (crew and passenger accommodations) |  | Basic and Extended
| (Green 93 deg C and Red 68 deg. C) | [6 empty] | Initial, Basic and Extended
Scope of Testing Conducted at this time: | Basic | [6 empty] | Yes
Initial testing completed: | N/A | Date completed: | [5 empty] | No
Basic testing completed: | Yes | Date completed: | [5 empty] | N/A
Extended testing compelted: | N/A | Date completed:
Note on D3: Insert date(s) of testing.
Note on D8: Enter date installed on board or Date of Build if system installed at time of new build.
Note on E8: State the minimum operating pressure stated on type approval certification.
Note on F8: State the Maximum operating pressure stated on the Type Approval Certification or Makers manual.
Note on G8: State the total number of nozzles/sprinklers installed for each make/type of system onboard.
Note on H8: State the total number of sections in which each make/type of system is fitted
Note on B18: Select the appropriate scope of testing from the drop down list
Note on B19: Only to be completed once all Initial testing completed. If all Initial testing is not applicable select N/A from drop down list
Note on D19: Enter Date all Initial testing Completed
Note on B20: Only to be completed once all Basic testing completed. If all Basic testing has not been completed select N/A from drop down list
Note on D20: Enter Date all Basic testing completed.
Note on B21: Only to be completed once all Extended testing completed. If all Extended testing has not been completed select N/A from drop down list.
Note on D21: Enter Date all Extended testing completed.

## Results
Test Results
Ship Name: | 0
IMO Number: | 0
Water Sample
Test No. | Section | Deck | MVZ | Area | Sprinkler Data | Position relative to Section valve | Release at Pilot Pressure? Y/N | Actual Release Pressure | Sprinkler distance from main line (m) | Filter Condition | pH | ConductivityμS/cm | Chlorides ppm | Date Tested | Observations/Comments
1 | 7.02 | Sun Deck | 3 | Fwd crew staircase |  |  |  | 7.5 bar |  |  | 6.5 | 320 | 60 | 2015-02-01 | Satisfactory | Far
2 | 7.03 | Bridge Deck | 4 | Aft crew staircase |  |  |  | 7.5 bar |  |  | 6.5 | 326 | 60 | 2015-02-01 | Satisfactory | Middle
3 | 7.01 | Bridge Deck | 2 | Fwd crew stair case |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory | Close
4 | 5.04 | Main Deck | 4 | Service Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
5 | 7.02 | Bridge Deck | 3 | Hotel Locker |  |  |  | 7.5 bar |  |  | 6.5 | 320 | 60 | 2015-02-01 | Satisfactory
6 | 5.01 | Platform 2 | 1 | Bosun Store |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory
7 | 3.03 | Platform 1 | 3 | Garbage Room |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory
8 | 3.01 | B Deck | 1 | Forward crew staircase |  |  |  | 7.5 bar |  |  | 6.5 | 326 | 60 | 2015-02-01 | Satisfactory
9 | 3.03 | Platform 1 | 3 | Incinerator Room |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory
10 | 5.02 | A Deck | 2 | Forward Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory
11 | 5.04 | A Deck | 4 | Aft Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
12 | 5.02 | Main Deck | 2 | Forward Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 324 | 60 | 2015-02-01 | Satisfactory
13 | 4.01 | B Deck | 4 | Aft Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
14 | 3.02 | Platform 1 | 2 | Provision Area |  |  |  | 7.5 bar |  |  | 6.5 | 328 | 60 | 2015-02-01 | Satisfactory
15 | 3.02 | B Deck | 2 | Outside Engine Room Casing |  |  |  | 7.5 bar |  |  | 6.5 | 328 | 60 | 2015-02-01 | Satisfactory
16 | 5.04 | Main Deck | 4 | Aft Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
17 | 5.04 | Main Deck | 4 | Aft Crew Staircase |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
18 | 4.01 | B Deck | 4 | Crew Galley |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
19 | 5.04 | A Deck | 4 | Main Galley |  |  |  | 7.5 bar |  |  | 6.5 | 329 | 60 | 2015-02-01 | Satisfactory
20 | 3.02 | B Deck | 2 | Cross Alleyway |  |  |  | 7.5 bar |  |  | 6.5 | 328 | 60 | 2015-02-01 | Satisfactory
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45
46
47
48
49
Note on D6: Main Vertical Zone
Note on F6: Enter Sprinkler type & serial number.
Note on G6: Select the appropriate position from the drop down list based on position with respect to arrangement of section
Note on H6: Enter "Y" if operated at Pilot pressure. Enter "N" if did not operate at pilot pressure. If operated after short delay at pilot pressure comment is to be made in the Observations/Comments column.
Note on I6: Only required for Extended testing. Actual release pressure to be stated. If no release at maximum operating pressure state "no release".
Note on J6: Enter distance of sprinkler/nozzle from main line.
Note on K6: State condition of filter, where fitted. Makers manual requirements/recommendations to be taken into consideration. "Satisfactory", "dirty", "blocked", etc.
Note on O6: Where water sample is tested in laboratory ashore this is to be stated in the observations/comments column.